## Storage Tank
Thermal Storage Tank Size Computation
3 tons of energy | 10543.5 | Watts | Note: These are known values; therefore, they do not change.
Require Usage Time | 12 | hr
Required stored energy | 455784.192 | KJ
Storage Tank Water Initial Temperature | 20 | C
Specific Heat of Water | 4.2 | KJ/kgK
Required Heat Transfer to cool the water from 20 to 0 degrees celcius | 114731.4118 | KJ
Required Mass of Ice | 1365.8501 | Kg
Volume of ice | 1.4895 | m^3
Required energy to convert water to ice @ 0 degrees celcius | 455784.192 | KJ
Total heat transfer to transform water to ice starting at 20 degrees celcius | 570515.6038 | KJ
Maximum Time available for freezing the whole volume of ice | 156 | hrs
Velocity glycol in intial coil before separation | 3 | m/s | Note: Green cells are input values
Surface Temperature on the coils 1st state | 290.3912 | K | Note: Usegoalseek on cell B 77 and set it to zero in order to calculate the surface temperature
Surface Temperature on the coils 2nd state | 286.7061 | K | Note: Usegoalseek on cell B 78 and set it to zero in order to calculate the surface temperature
Surface Temperature on the coils 3rd state | 276.4907 | K | Note: Usegoalseek on cell B 79 and set it to zero in order to calculate the surface temperature
Surface Temperatue on the coils Final state | 271.8883 | K | Note: Usegoalseek on cell B 80 and set it to zero in order to calculate the surface temperature
Diameter of initial coil before separation | 0.05 | m
Diameter of coils after separation | 0.024 | m
Length of coils | 13 | m
Number of Coils | 32
Tank Length | 1.2 | m
Surface Area of one coil after separation | 0.98018 | m^2
Total surface area off all coils | 31.3657 | m^2
Area of one coil after separation | 0.00045239 | m^2
Area of all coils after separation | 0.014476 | m^2
Volume of all coils after separation | 0.18819 | m^3
Area of initial coil before separation | 0.0019635 | m^2
Mass flow rate glycol in initial coil before separation | 6.5326 | kg/s
Volume flow rate glycol in initial coil before separation | 0.0058905 | m^3/s
Minumum power required in order to freeze all the water in the specified amount of time | 1015.8754 | w
Temperature @ which glycol is entering the tank | 263 | K
Temperature of water @ initial state | 293 | K
Temperature of water @ final state | 273 | K
Film Temperature on water side @ initial state | 291.6956 | K
Ra of Water at initial state | 304442.0415 | Ra number is correct
Nusselt Number after calculating Ra | 12.8937
Heat transfer coefficient for initial state on the outside (Water side) | 316.4323 | w/m^2 k
Temperature of water @ second state | 288 | K
Film Temperature of water second state | 287.353
Ra of water at second state | 710250.2462 | Ra number is correct
Nusselt Number after calculating Ra 2nd phase | 16.4836
Heat transfer coefficient for second state on the outside (water side) | 398.3543 | w/m^2 k
Temperature of water @ third state | 278 | K
Film Temperature of water third state | 277.2454 | K
Ra number of water at third state | 14876.0262 | Ra number is correct
Nusselt Number after calculating Ra 3rd state | 5.8805
Heat transfer coefficient for third state on the outside (water side) | 139.907 | w/m^2 k
Temperature of water @ final state | 273 | K
Film Temperature of water final state | 272.4442 | K
Ra number of water at Final state | 43019.0409
Nusselt Number after calculating Ra Final State | 7.7756
Heat transfer coeffient for Final state on the outside (Water side) | 181.7539 | w/m^2 k
Glycol entering temperature | 263 | K
Nusselt Number of glycol inside coils | 3.66 |  | Note: This will change depending if it is laminar or turbulent. For laminar is 3.66 but for turbulent it will change
Heat transfer coefficient inside coils | 36.905 | w/m^2 k
Overall Heat transfer coefficient initial state | 33.0504 | w/m^2 k
Overall Heat transfer coefficient Second state | 33.7759 | w/m^2 k
Overall Heat transfer coefficient Third state | 29.202 | w/m^2 k
Overall Heat transfer coefficient Final state | 30.6762 | w/m^2 k
Exit Temperature of Glycol initial state | 264.8308 | K
Exit Temperature of Glycol Second state | 264.618 | K
Exit Temperature of Glycol Third state | 263.7999 | K
Exit Temperature of Glycol Final state | 263.5528 | K
Log mean temperature difference 1 | 26.4653 | K
Log mean temperature difference 2 | 22.8875 | K
Log mean temperature difference 3 | 13.0867 | K
Log mean temperature difference 4 | 8.609 | K
Heat loss inside coil intial state | 857.3503 | w
Heat loss inside coil Second state | 757.7244 | w
Heat loss inside coil Third state | 374.5834 | w
Heat loss inside coil Final state | 258.8571 | w
Heat loss in water initial state | 809.1467 | w
Heat loss in water Second state | 505.2207 | w
Heat loss in water Third state | 206.9748 | w
Heat loss in water Final state | 198.0445 | w
Heat loss comparison 1 | 48.2036 | w
Heat loss comparison 2 | 252.5037 | w
Heat loss comparison 3 | 167.6086 | w
Heat loss comparison 4 | 60.8126 | w
Total heat loss adding all the coils initial state | 27435.2094 | w
Total heat loss adding all the coils second state | 24247.1822 | w
Total heat loss adding all the coils third state | 11986.6692 | w
Total heat loss adding all the coils Final state | 8283.4268 | w
Energy required to lower the water temperature by 5 degrees | 28682852.9577 | J
Energy required to lower the water temperature by 8 degrees | 45892564.7324 | J
Energy required to lower the water temperature by 7 degrees | 40155994.1408 | J
Energy required to freeze the water at 0 degrees | 455784192 | J
Require time in order to finish the Initial state | 0.29041 | Hrs
Require time in order to finish the Second state | 0.52575 | Hrs
Require time in order to finish the Third state | 0.93057 | Hrs
Require time in order to finish the Final state | 15.2843 | Hrs
Maximum amount of time | 156 | Hrs
Time required to freeze the water by adding the time calculations | 17.0311 | Hrs
Chiller Selection
Power needed to lower the temeperature of glycol | 27435.2094 | w
Pump Selection
Reynolds number on the coil before separation | 7799.2405
Friction Factor on bigger coil | 0.033024
Length on bigger coil | 1.2 | m
Frictional loss on bigger coil | 0.36356 | m
Frictional loss on one small coil | 0.57614 | m
Frictional loss on all small coils | 18.4365 | m
Sum of all frictional losses | 18.8001 | m
Minor Losses on bigger coil
Ball Valve K | 0.05
90 degree elbow | 0.31
Minor loss on bigger coil calculation | 0.16514 | m
Minor losses on small coil
Sudden Contraction | 2.5754
Sudden Expansion | 11.1575
180 elbows | 0.3
# of elbows | 9
Minor loss on small coil | 0.13867 | m
Minor loss on all small coils | 4.4375 | m
Sum of all losses (Head loss) | 23.4028 | m
Output power required by a pump | 1499.7545 | w
Volume flow rate in gal/min | 93.3663 | gal/min
Head loss in ft | 76.7808 | ft
Post analysis in the process (2nd system)
Initial Temperature of glycol in the air conditioner | 265 | K
Diameter of tube | 0.05 | m
Velocity inside the tube | 3 | m/s
Power needed in order to melt all the ice | 10550.56 | w
Temperature of air | 293 | K
Velocity of air | 2 | m/s
Mass flow rate of glycol | 6.5326 | kg/s
Inside analysis
Reynolds number | 7799.2405
Nusselt Number on the inside | 291.606
Heat transfer coefficient on the inside | 1411.3729 | w/m^2-K
These calculations are for the A/C unit
Effectiveness NTU-Method
Post analysis in the process
Mass flow rate of glycol | 6.5326 | kg/s
Side length of the frontal area | 1.7 | m
Frontal area of the heat exchanger | 2.89 | m^2
Velocity of air | 2 | m/s
Mass flow rate of air | 6.9591 | kg/s
Capacitance of glycol | 14985.703
Capacitance of air | 7007.8338
Capacity Ratio | 0.46763
Qmax | 196219.3475 | w
Effectiveness (E) | 0.053769
Hydraulic Diameter | 1.445
Reynolds Number in the air side | 190633.2454
Nusselt Number | 276.7627
Heat transfer coefficient | 139.1563
Number of transfer units NTU | 0.055996
Surface area on the tube | 2.8199 | m^2
Length of the tube | 17.952 | m
Exit temperature of glycol | 265.704 | K
Heat transfer | 10550.56 | w
# of tube turns | 10.56
St or separation between each turn | 0.27197 | m
Pump Selection # 2
Friction Factor | 0.033024
Frictional Loss | 5.4389 | m
Minor Losses
# 180 elbow | 10
180 elbow k loss | 0.3
ball valve | 0.05
Minor Loss | 1.422 | m
Sum or all loses | 6.8609 | m
Work output pump needed | 439.6784 | w
Total Tank Volume | 1.6777 | m^3
Tank width | 2.368 | m
Tank Height | 0.5904 | m
Tank Length | 1.2 | m
St of small coils | 0.054498
Tank Insulation
Surface are of the tank | 9.8963 | m^2
Insulation Thickness 1 | 0.02 | m
Insulation Thickness 2 | 0.2 | m
Insulation Thickness 3 | 0.3 | m
Resistance on the insulation | 127.7064
Heat transfer through the insulation | 0.15661 | w
Insulator Aluminum foil & polyurethane foam
Thermal conductivity aluminum foil | 1.7e-05 | w/m k
Thermal conductivity polyurethane foam | 0.0023 | w/m k
Thermal conductivity concrete | 0.77 | w/m k
Cost Analysis
Length of small coils (0.05)
Length of large tubes (0.1) | 416 | m | Total cost of small coils | 3440.32
Diameter of small coils | 19.152 | m | Total cost of large coils | 344.7366
Diameter of large coils | 0.05 | m | Total cost | 5110.0566
Volume of aluminum foil | 0.1 | m
Volume of polyurethane foam | 0.19793 | m^3 | 3-ton air conditioner price | 3200
Volume of concrete | 1.9793 | m^4 | Difference in price | 1910.0566
Cost of of small coils | 2.9689 | m^5
Cost of large coils | 8.27 | $/m
Chiller | 18 | $/m
Tank material | 350 | $
Aluminum foil | 75 | $
Polyurethane foam | 100 | $
Pumps | 300 | $
Ball valves (3) | 200 | $
| 300 | $
Operating Cost
On-Peak hrs
Off Peak hrs | 0.21 | $/kw-h
3-ton air conditioner power input | 0.068 | $/kw-h
3-ton air conditioner | 20 | kw-hr
By usign the thermal storage tank | 705.6 | $/yr
Power input | 335.5759 | $/yr
Difference in price | 29.3746 | Kw
In how much time it is going to be paid off | 370.0241
| 5.162 | Yrs
Velocity of coil 1
Velocity of coil 2 | 0.4069 | m/s
Velocity of coil 3 | 0.4069 | m/s
Velocity of coil 4 | 0.4069 | m/s
Velocity of coil 5 | 0.4069 | m/s
Velocity of coil 6 | 0.4069 | m/s
Velocity of coil 7 | 0.4069 | m/s
Velocity of coil 8 | 0.4069 | m/s
Velocity of coil 9 | 0.4069 | m/s
Velocity of coil 10 | 0.4069 | m/s
Velocity of coil 11 | 0.4069 | m/s
Velocity of coil 12 | 0.4069 | m/s
Velocity of coil 13 | 0.4069 | m/s
Velocity of coil 14 | 0.4069 | m/s
Velocity of coil 15 | 0.4069 | m/s
Velocity of coil 16 | 0.4069 | m/s
Volume flow rate 1 | 0.4069 | m/s
Volume flow rate 2 | 0.00018408 | m^3/s
Volume flow rate 3 | 0.00018408 | m^3/s
Volume flow rate 4 | 0.00018408 | m^3/s
Volume flow rate 5 | 0.00018408 | m^3/s
Volume flow rate 6 | 0.00018408 | m^3/s
Volume flow rate 7 | 0.00018408 | m^3/s
Volume flow rate 8 | 0.00018408 | m^3/s
Volume flow rate 9 | 0.00018408 | m^3/s
Volume flow rate 10 | 0.00018408 | m^3/s
Volume flow rate 11 | 0.00018408 | m^3/s
Volume flow rate 12 | 0.00018408 | m^3/s
Volume flow rate 13 | 0.00018408 | m^3/s
Volume flow rate 14 | 0.00018408 | m^3/s
Volume flow rate 15 | 0.00018408 | m^3/s
Volume flow rate 16 | 0.00018408 | m^3/s
Reynolds number 1 | 0.00018408 | m^3/s
Reynolds number 2 | 507.7631
Reynolds number 3 | 507.7631
Reynolds number 4 | 507.7631
Reynolds number 5 | 507.7631
Reynolds number 6 | 507.7631
Reynolds number 7 | 507.7631
Reynolds number 8 | 507.7631
Reynolds number 9 | 507.7631
Reynolds number 10 | 507.7631
Reynolds number 11 | 507.7631
Reynolds number 12 | 507.7631
Reynolds number 13 | 507.7631
Reynolds number 14 | 507.7631
Reynolds number 15 | 507.7631
Reynolds number 16 | 507.7631
Friction Factor f 1 | 507.7631
Friction Factor f 2 | 0.12604
Friction Factor f 3 | 0.12604
Friction Factor f 4 | 0.12604
Friction Factor f 5 | 0.12604
Friction Factor f 6 | 0.12604
Friction Factor f 7 | 0.12604
Friction Factor f 8 | 0.12604
Friction Factor f 9 | 0.12604
Friction Factor f 10 | 0.12604
Friction Factor f 11 | 0.12604
Friction Factor f 12 | 0.12604
Friction Factor f 13 | 0.12604
Friction Factor f 14 | 0.12604
Friction Factor f 15 | 0.12604
Friction Factor f 16 | 0.12604
Pressure Drop 1 | 0.12604
Pressure Drop 2 | 6268.0167 | Pa
Pressure Drop 3 | 6268.0167 | Pa
Pressure Drop 4 | 6268.0167 | Pa
Pressure Drop 5 | 6268.0167 | Pa
Pressure Drop 6 | 6268.0167 | Pa
Pressure Drop 7 | 6268.0167 | Pa
Pressure Drop 8 | 6268.0167 | Pa
Pressure Drop 9 | 6268.0167 | Pa
Pressure Drop 10 | 6268.0167 | Pa
Pressure Drop 11 | 6268.0167 | Pa
Pressure Drop 12 | 6268.0167 | Pa
Pressure Drop 13 | 6268.0167 | Pa
Pressure Drop 14 | 6268.0167 | Pa
Pressure Drop 15 | 6268.0167 | Pa
Pressure Drop 16 | 6268.0167 | Pa
Pressure change for calculations | 6268.0167 | Pa
Mass flow continuity | 0 | Pa
Mass flow rate coil 1 | 0.0029453 | m^3/s
Mass flow rate coil 2 | 0.20414 | kg/s
Mass flow rate coil 3 | 0.20414 | kg/s
Mass flow rate coil 4 | 0.20414 | kg/s
Mass flow rate coil 5 | 0.20414 | kg/s
Mass flow rate coil 6 | 0.20414 | kg/s
Mass flow rate coil 7 | 0.20414 | kg/s
Mass flow rate coil 8 | 0.20414 | kg/s
Mass flow rate coil 9 | 0.20414 | kg/s
Mass flow rate coil 10 | 0.20414 | kg/s
Mass flow rate coil 11 | 0.20414 | kg/s
Mass flow rate coil 12 | 0.20414 | kg/s
Mass flow rate coil 13 | 0.20414 | kg/s
Mass flow rate coil 14 | 0.20414 | kg/s
Mass flow rate coil 15 | 0.20414 | kg/s
Mass flow rate coil 16 | 0.20414 | kg/s
| 0.20414 | kg/s

## Properties
Properties of Water at 0 |  |  | Properties of water from 25 to 0 |  |  | Properties of Glycol |  |  | Properties of air
Latent heat of Fusion of water | 333.7 | KJ/Kg | Cp of water ranging from 0 to 26.66 C | 4.2 | KJ/KgK | Cp of Ethyene Glycol | 2294 | J/KgK | Density of air | 1.204 | kg/m^3 | at 20
Density of ice | 917 | Kg/m^3 | Pr of water @ 10 | 9.45 |  | Density of glycol room temp | 1109 | kg/m^3 | Pr | 0.7309
Pr of water at 0 | 13.5 |  | B volume expansion @ 10 | 0.000733 | 1/k | Dynamic Viscosity | 0.021329 | kg/m s | Kinematic Viscocity | 1.516e-05 | m^2/s
B volume expansion water at 0 | -6.8e-05 | 1/k | Dynamic viscosity @ 10 | 0.001307 | kg/m*s | Pr of Glycol | 615 |  | Thermal conductivity | 0.02514 | w/m*K
Dynamic viscosity at 0 | 0.001792 | kg/m*s | Thermal conductivity @ 10 | 0.58 | w/m*k | Thermal conductivity | 0.242 | w/m*k | Cp | 1007 | J/kg*K
Thermal conductivity at 0 | 0.561 | w/m*k | Pr of water @ 15 | 8.09
|  |  | B volume of expansion @ 15 | 0.000138 | 1/k
|  |  | Dynamic viscosity @ 15 | 0.001138 | kg/m*s
|  |  | Thermal conductivity @ 15 | 0.589 | w/m*k
|  |  | Pr of water @ 5 | 11.2
|  |  | B volume expansion @ 5 | 1.5e-05 | 1/k
|  |  | Dynamic viscosity @ 5 | 0.001519 | kg/m*s
|  |  | Thermal conductivity @ 5 | 0.571 | w/m*k
|  |  | Pr of water @ 0 | 13.5
|  |  | B volume expansion @ 0 | -6.8e-05 | 1/k
|  |  | Dynamic viscosity @ 0 | 0.001792 | kg/m*s
|  |  | Thermal conductivity @ 0 | 0.561 | w/m*k